## INSTRUMENT LIST
| PT | SW | PT | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS | PT | 1/2" NPT (F) | PT | 6" |  |  | PT | DIAPHARGM
| LT | SW | LT | TEMPENSE/GIC/RADIX/ALTOP | LT | 1/2" NPT (F) | LT | 6" |  |  | LT | DP
| FT | SW | FT | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL | FT | 1/2" NPT (F) | FT | 6" |  |  | FT | DP
| TE | SW | TE | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL | TE | 1/2" NPT (F) | TE | - |  |  | TE | RTD-PT100/K TYPE (DUPLEX)
| PI | SW | PI | FORBES/GENERAL/WAAREE | PI | 1/2" NPT (F) | PI | 6" |  |  | PI | BOURDON TUBE
| TI | SW | TI | FORBES/GENERAL/WAAREE | TI | 1/2" NPT (F) | TI | 6" |  |  | TI | Bi-METAL
| LG | FE, #150 | LG | FORBES/GENERAL/WAAREE | LG | 25 | LG | - |  |  | LG | GLASS TUBE/REFLEX
| LS | SW | LS | V AUTOMATE/LEVCON | LS | 25 | LS | - |  |  | LS | CAPACITIVE/FORK TYPE
| PS | SW | PS | BAUMER/DANFOSS/INDFOS | PS | 25 | PS | - |  |  | PS | ELECTRIMECHANICAL/ SOLID-STATE
| DT | SW | PT | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL | DT | 1/2" NPT (F) | DT | 6" |  |  | DT | DIAPHARGM
| ZSS | - | ZSS | ELECTRONIC SPEED SWITCH | ZSS | - | ZSS | - |  |  | ZSS | SPST
| DPT | SW | DPT | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL | DPT | 25 | DPT | 6" |  |  | DPT | DP
SR.NO. | DESIGN PRESSURE | DESIGN TEMP | TAG NO | LOCATION | MEDIUM | TYPE | SIZE | DIAL SIZE | END | QUANTITY | TYPE | MAKE | INSERTION LENGTH | R
| DEG C - KG/CM2/ MMWC | °C |  |  |  |  | NB | [5 empty] | mm
1 | STEAM & WATER CIRCUIT
1 | 25 | 121 | PT-0401 | BAYPASS TO DEARATOR LINE | WATER | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
2 | 25 | 121 | PI-0401 | DEARATOR TO HP HEATER P-101 OUTLET LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
3 | 25 | 121 | PI-0402 | DEARATOR TO HP HEATER P-101 OUTLET LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
4 | 25 | 121 | TI-1106 | DEARATOR TO HP HEATER LINE | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
5 | 25 | 121 | PI-1106 | DEARATOR TO HP HEATER LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
6 | 24 | 184.5 | TI-1107 | FLASH VESSEL TO HP HEATER LINE | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
7 | 24 | 184.5 | PI-1107 | FLASH VESSEL TO HP HEATER LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
8 | 32 | 202.4 | PI-0403 | FLASH VESSEL TO SG & FG COLLER LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
9 | 32 | 202.4 | PI-0404 | FLASH VESSEL TO SG & FG COLLER LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
10 | 32 | 202.4 | PT-0402 | SG & FG COOLET WATER INLET COMMON HEADER | WATER | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
11 | 32 | 202.4 | FT-0401 | SYNGAS COOLER WATER INLET LINE | WATER | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
12 | 32 | 202.4 | PI-0405 | SYNGAS COOLER WATER INLET LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
13 | 32 | 202.4 | TI-0402 | SYNGAS COOLER WATER INLET LINE | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
14 | 32 | 202.4 | FT-0402 | FLUE GAS COOLER WATER INLET LINE | WATER | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
15 | 32 | 202.4 | PI-0406 | FLUE GAS COOLER WATER INLET LINE | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
16 | 32 | 202.4 | TI-0401 | FLUE GAS COOLER WATER INLET LINE | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
17 | 30 | 224.7 | PI-0408 | SYNGAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
18 | 30 | 224.7 | TI-0403 | SYNGAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
19 | 30 | 224.7 | FT-0403 | SYNGAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
20 | 30 | 224.7 | PI-0407 | FLUE GAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
21 | 30 | 224.7 | TI-0404 | FLUE GAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
22 | 30 | 224.7 | FT-0404 | FLUE GAS COOLER WATER OUTLET LINE TO FLASH TANK | WATER | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
23 | 16 | 203.5 | LG-0401 | FLASH VESSEL TANK | STEAM | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
24 | 16 | 203.5 | LG-1101 | FLASH VESSEL TANK | STEAM | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
25 | 16 | 203.5 | LT-0401 | FLASH VESSEL TANK | STEAM | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
26 | 16 | 203.5 | LS-0401 | FLASH VESSEL TANK | STEAM | LS | 25 | - | SW | 1 | CAPACITIVE/FORK TYPE | V AUTOMATE/LEVCON
27 | 16 | 203.5 | PI-0409 | MP STEAM LINE TO STEAM HEADER | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
28 | 16 | 203.5 | PT-0403 | MP STEAM LINE TO STEAM HEADER | STEAM | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
29 | 16 | 203.5 | FT-0405 | MP STEAM LINE TO STEAM HEADER | STEAM | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
2 | GASIFIRE SYSTEM
30 | 1.99 | 680 | PT-0102A | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
31 | 1.99 | 680 | PT-102B | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
32 | 1.99 | 680 | PT-102C | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
33 | 1.99 | 680 | TE-0101 | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
34 | 1.99 | 680 | PT-0101 | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
35 | 1.99 | 680 | TE-0102A | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP | TEMPENSE/GIC/RADIX/ALTOP
36 | 1.99 | 680 | TE-0102B | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
37 | 1.99 | 680 | TE-0102C | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
38 | 1.99 | 680 | PT-0103A | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
39 | 1.99 | 680 | PT-0103B | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
40 | 1.99 | 680 | PT-0103C | GASIFIRE R01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
41 | 1.99 | 680 | TE-0103A | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
42 | 1.99 | 680 | TE-0103B | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
43 | 1.99 | 680 | TE-0103C | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
44 | 1.99 | 680 | TE-0104A | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
45 | 1.99 | 680 | TE-0104B | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
46 | 1.99 | 680 | TE-0104C | GASIFIRE R01 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
47 | 1.99 | 680 | DPT-0101A | GASIFIRE R01 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
48 | 1.99 | 680 | DPT-0101B | GASIFIRE R01 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
49 | 1.99 | 680 | DPT-0101C | GASIFIRE R01 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
50 | 2.13 | 760.1 | PT-0104A | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
51 | 2.13 | 760.1 | PT-0104B | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
52 | 2.13 | 760.1 | PT-0104C | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
53 | 2.13 | 760.1 | PT-0105A | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
54 | 2.13 | 760.1 | PT-0105B | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
55 | 2.13 | 760.1 | PT-0105C | COMBUSTOR R02 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
56 | 2.13 | 760.1 | TE-0105A | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
57 | 2.13 | 760.1 | TE-0105B | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
58 | 2.13 | 760.1 | TE-0105C | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
59 | 2.13 | 760.1 | TE-0106A | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
60 | 2.13 | 760.1 | TE-0106B | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
61 | 2.13 | 760.1 | TE-0106C | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
62 | 2.13 | 760.1 | TE-0107A | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
63 | 2.13 | 760.1 | TE-0107B | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
64 | 2.13 | 760.1 | TE-0107C | COMBUSTOR R02 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
65 | 2.13 | 760.1 | DPT-0102A | COMBUSTOR R02 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
66 | 2.13 | 760.1 | DPT-0102B | COMBUSTOR R02 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
67 | 2.13 | 760.1 | DPT-0102C | COMBUSTOR R02 | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
68 | 2.13 | 760.1 | DPT-0103 | SYNGAS & FLUE GAS COOLER LINE | GAS | DPT | 25 | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
69 | 2.13 | 760.1 | TE-0108 | COMBUSTOR R02 TO FLUE GAS COOLER LINE | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
70 | 2.13 | 760.1 | PT-106 | COMBUSTOR R02 TO FLUE GAS COOLER LINE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
71 | 1.55 | 760.1 | PT-107 | COMBUSTOR R02 TO FLUE GAS COOLER LINE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
72 | 1.55 | 760.1 | TE-0109 | COMBUSTOR R02 TO FLUE GAS COOLER LINE | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
3 | SYNGAS SYSTEM
73 | 1.99 | 680 | PI-0201 | GASIFIRE TO SYN GAS COOLER LINE | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
74 | 1.99 | 680 | TG-0201 | GASIFIRE TO SYN GAS COOLER LINE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
75 | 1.99 | 680 | PT-0202 | GASIFIRE TO SYN GAS COOLER LINE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
76 | 1.99 | 680 | TE-0201 | GASIFIRE TO SYN GAS COOLER LINE | GAS | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
77 | 1.99 | 680 | PI-0201 | SYNGAS COOLER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | TEMPENSE/GIC/RADIX/ALTOP
78 | 1.99 | 680 | TI-0201 | SYNGAS COOLER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
79 | 1.99 | 680 | TI-0201 | SYNGAS COOLER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
80 | 1.38 | 231.5 | PT-0203 | SYNGAS COOLER OUTLET | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
81 | 1.38 | 231.5 | TE-0202 | SYNGAS COOLER OUTLET | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
82 | 1.38 | 231.5 | PI-0204 | SYNGAS COOLER OUTLET | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | TEMPENSE/GIC/RADIX/ALTOP
83 | 1.38 | 231.5 | TI-0202 | SYNGAS COOLER OUTLET | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
84 | 1.33 | 231.5 | TE-0203 | CHAR+ASH FILTER |  | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
85 |  |  | PT-0207 | NITROGEN PURGING TANK |  | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
86 | 1.33 | 231.5 | DPT-0201 | CHAR+ASH FILTER |  | DPT | 25 | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
87 | 1.33 | 231.5 | LS-0201 | CHAR+ASH FILTER |  | LS | 25 | - | SW | 1 | CAPACITIVE/FORK TYPE | V AUTOMATE/LEVCON
88 |  |  | PI-0208 | NITROGEN FROM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
89 | 1.33 | 230.8 | PT-205 | CHAR+ASH FILTER TO COMBUSTOR LINE |  | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
90 | 1.33 | 231.5 | PI-0206 | PRODUCT GAS CATALYST SYSTEM | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
91 | 1.33 | 231.5 | TE-0203 | PRODUCT GAS CATALYST SYSTEM | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
92 | 1.33 | 231.5 | TI-0203 | PRODUCT GAS CATALYST SYSTEM | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
4 | SYNGAS SYSTEM
93 | 0.04 | 760.2 | PI-301 | BEFORE FLUE GAS COOLER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
94 | 0.04 | 760.2 | TG-0301 | BEFORE FLUE GAS COOLER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
95 | 0.04 | 760.2 | PT-0302 | BEFORE FLUE GAS COOLER | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
96 | 0.04 | 760.2 | TE-0301 | BEFORE FLUE GAS COOLER | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
97 | 0.04 | 760.2 | PI-303 | FLUE GAS COOLER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | TEMPENSE/GIC/RADIX/ALTOP
98 | 0.04 | 760.2 | TI-303 | FLUE GAS COOLER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
99 | 0.02 | 231.5 | TE-0302 | BEFORE BAG FILTER | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
100 | 0.02 | 231.5 | PT-0304 | BEFORE BAG FILTER | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
101 | 0.02 | 231.5 | TE-0303 | FLUE GAS BAG FILTER | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
102 | 0.02 | 231.5 | LS-0301 | FLUE GAS BAG FILTER | GAS | LS | 25 | - | SW | 1 | CAPACITIVE/FORK TYPE | V AUTOMATE/LEVCON
103 | 0.02 | 231.5 | DPT-0301 | FLUE GAS BAG FILTER | GAS | DPT | 25 | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
104 |  | 45 | PT-0305 | AIR PURGING TANK | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
105 | 0.02 | 150 | PT-0306 | AFTER BAG FILTER | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
106 | 0.02 | 150 | TE-0304 | AFTER BAG FILTER | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
107 | 0.02 | 150 | FT-0302 | AFTER BAG FILTER | GAS | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
108 | 0.02 | 150 | ZSS1-0301 | FLUE GAS BAG FILTER RAV | GAS | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
5 | CATALYST SYSTEM
109 | 16 | 260 | PI-0501 | MP STEAM FOR SPENT CAT. HOPPER | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
110 | 16 | 260 | PI-0606 | PLANT AIR FOR SPENT CAT. HOPPER | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
111 | 16 | 260 | PI-0606 | PLANT AIR FOR FRESH CAT. HOPPER | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
6 | CMBUSTION SYSTEM
112 | 3 | 670 | PI-0606 | AFTER DFAH FOR COMBUSTOR | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
113 | 3 | 670 | PT-0603 | AFTER DFAH FOR COMBUSTOR | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
114 | 3 | 670 | FT-0603 | AFTER DFAH FOR COMBUSTOR | AIR | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
115 | 3 | 670 | PI-0605 | AFTER DFAH FOR COMBUSTOR | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
116 | 3 | 670 | PT-0604 | AFTER DFAH FOR COMBUSTOR | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
117 | 3 | 670 | FT-0602 | AFTER DFAH FOR COMBUSTOR | AIR | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
118 | 3 | 670 | PI-0604 | AFTER DFAH FOR COMBUSTOR | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
119 | 3 | 670 | TE-0601 | AFTER DFAH FOR COMBUSTOR | AIR | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
120 | 3 | 670 | PT-0602 | AFTER DFAH FOR COMBUSTOR | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
121 | 3 | 40 | PI-0607 | TAIL GAS FOR DFAH | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
122 | 3 | 40 | DPT-0601 | TAIL GAS FOR DFAH | GAS | DPT | 25 | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
123 | 3 | 40 | PI-0608 | TAIL GAS FOR DFAH | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
124 | 3 | 223.1 | PI-0602 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
125 | 3 | 223.1 | PT-0601 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
126 | 3 | 223.1 | FT-0601 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
127 | 3 | 223.1 | PI-0601 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
128 | 3 | 223.1 | PI-0603 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
129 | 3 | 223.1 | TE-0602 | COMBUSTION AIR BLOWER LINE FOR DFAH | AIR | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
7 | FUEL HANDLING SYSTEM
130 |  | 50 | ZSS-01 | BC-01 INCLINED BELT CONVEYOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
131 |  | 50 | ZSS-02 | BC-02 INCLINED BELT CONVEYOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
132 |  | 50 | ZSS-03 | BC-05 INCLINED BELT CONVEYOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
133 |  | 50 | ZSS-04 | BC-03 INCLINED BELT CONVEYOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
134 |  | 50 | ZSS-05 | BC-04 INCLINED BELT CONVEYOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
135 |  | 50 | ZSS-06 | ELV-01 OVER SIZE BUCKET ELEVATOR |  | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
136 |  | 120 | TE-02 | BEFORE COAL DRYER FROM FD FAN | AIR | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
137 |  | 120 | TG-02 | BEFORE COAL DRYER FROM FD FAN | AIR | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
138 |  | 120 | PG-01 | BEFORE COAL DRYER FROM FD FAN | AIR | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
139 |  | 120 | TE-01 | BEFORE BAG FILTER FROM COAL DRYAER | AIR | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
140 |  | 120 | TG-01 | BEFORE BAG FILTER FROM COAL DRYAER | AIR | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
141 |  | 50 | DT-01 | BM-01 BALL MILL |  | DT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
142 |  | 50 | LSH-01 | BIOMASS/COAL SORAGE SILO |  | LS | 25 | - | SW | 1 | CAPACITIVE/FORK TYPE | TEMPENSE/GIC/RADIX/ALTOP
143 |  | 50 | PG-04 | BIOMASS/COAL SORAGE SILO |  | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | TEMPENSE/GIC/RADIX/ALTOP
144 |  | 50 | LSL-01 | BIOMASS/COAL SORAGE SILO |  | LS | 25 | - | SW | 1 | CAPACITIVE/FORK TYPE | TEMPENSE/GIC/RADIX/ALTOP
145 |  | 50 | PT-06 | INSTRUMENT AIR FOR | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
146 |  | 50 | PI-05 | LH-01/CB-01 CHEMBER |  | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | TEMPENSE/GIC/RADIX/ALTOP
147 |  | 50 | LI-01 | LH-01 CHEMBER |  | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | TEMPENSE/GIC/RADIX/ALTOP
148 |  | 50 | LI-02 | CB-01 CHEMBER |  | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | TEMPENSE/GIC/RADIX/ALTOP
149 |  | 50 | PT-01 | NITROGEN FOR LH-01 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | TEMPENSE/GIC/RADIX/ALTOP
150 |  | 50 | LT-01 | CB-01 CHEMBER |  | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
151 |  | 50 | LT-02 | LH-01 CHEMBER |  | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
152 | 4.5 | 35 | TG-02 | CW OUTLET FROM SCREW FEEDER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | TEMPENSE/GIC/RADIX/ALTOP
153 | 4.5 | 35 | TE-02 | CW OUTLET FROM SCREW FEEDER | WATER | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
154 | 4.5 | 35 | PG-04 | CW INLET TO SCREW FEEDER | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
155 | 4.5 | 35 | TG-01 | CW INLET TO SCREW FEEDER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
156 | 4.5 | 35 | TE-01 | CW INLET TO SCREW FEEDER | WATER | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
157 | 4.5 | 35 | PT-06 | CW INLET TO SCREW FEEDER | WATER | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
158 | 4 | 35 | PT-02 | PLANT AIR FOR BALL MILL, HAMMER MILL & SILO | AIR | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
8 | MP STEAM SYSTEM
159 | 16 | 204 | PI-0901 | BEFORE ELECTRICAL STEAM SUPERHEATER | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
160 | 16 | 204 | TI-0901 | BEFORE ELECTRICAL STEAM SUPERHEATER | STEAM | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
161 | 15.49 | 420 | TE-0902 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | TE | 1/2" NPT (F) | - | SW | 1 | K TYPE (DUPLEX) | TEMPENSE/GIC/RADIX/ALTOP
162 | 15.49 | 420 | FT-0901 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
163 | 15.49 | 420 | FT-0902 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
164 | 15.49 | 420 | PI-0902 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
165 | 15.49 | 420 | PI-0903 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
166 | 15.49 | 420 | TI-0903 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
167 | 15.49 | 420 | TI-0904 | AFTER ELECTRICAL STEAM SUPERHEATER FOR GASIFIRE | STEAM | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
9 | CHAR+ASH FEEDING SYSTEM
168 |  | 50 | PT-1001 | NITROGEN FOR SCREW | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
169 |  | 50 | PI-1002 | NITROGEN FOR SCREW | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
170 |  | 50 | PT-1003 | NITROGEN FOR SCREW | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
171 |  | 50 | PI-1004 | NITROGEN FOR SCREW | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
172 | 4.5 | 35 | PI-1005 | COOLING WATER FOR SCREW | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
173 | 4.5 | 35 | TE-10001 | COOLING WATER FOR SCREW | WATER | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
174 | 4.5 | 35 | FT-1001 | COOLING WATER FOR SCREW | WATER | FT | 1/2" NPT (F) | 6" | SW | 1 | MASS FLOW / VERTEX | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
175 |  |  | ZSS-1001 | SCREW | WATER | ZSS | - | - | - | 1 | SPST | ELECTRONIC SPEED SWITCH
10 | SYNGAS SCRUBBER SYSTEM
176 |  | 50 | PI-1116 | NITROGEN FOR V01 SOTAGE TANK | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
177 |  | 50 | PI-1117 | NITROGEN FOR V01 SOTAGE TANK | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
178 | 5 | 120 | PS-1101 | V01 SOTAGE TANK | GAS | PS | 25 | - | SW | 1 | ELECTRIMECHANICAL/ SOLID-STATE | BAUMER/DANFOSS/INDFOS
179 | 5 | 120 | LG-1101 | V01 SOTAGE TANK | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
180 | 5 | 120 | TE-1101 | V01 SOTAGE TANK | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
181 | 5 | 120 | LT-1101 | V01 SOTAGE TANK | GAS | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
182 | 5 | 120 | LG-1103 | COLD CSO | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
183 | 0.85 | 89.1 | PI-1112 | V01 SOTAGE TANK TO SCRUBBER LINE | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
184 | 0.85 | 89.1 | TI-1112 | V01 SOTAGE TANK TO SCRUBBER LINE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
185 | 0.85 | 89.1 | TE-1105 | SYNGASS CLEANING FROM SCRUBBER | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
186 | 1.02 | 284.1 | PI-1115 | CSO FOR SCRUBBER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
187 | 1.02 | 284.1 | TI-1114 | CSO FOR SCRUBBER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
188 | 0.85 | 89.1 | LT-1102 | SCRUBBER TANK | GAS | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
189 |  |  | PI-1113 | FOR CSO FROM SCRUBBER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
190 | 0.92 | 192.1 | PI-1105 | AFTER BFW HEATER FROM SCRUBBER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
191 | 0.92 | 192.1 | TI-1104 | AFTER BFW HEATER FROM SCRUBBER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
192 | 1.02 | 284.1 | TI-1103 | AFTER CSO SHIFT R05 FROM BFW HEATER | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
193 | 1.02 | 284.1 | PI-1104 | AFTER CSO SHIFT R05 FROM BFW HEATER | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
194 | 16 | 260 | FT-0502 | MP STEAM FOR CSO SHIFT R05 | STEAM | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
195 | 16 | 260 | PT-1101 | MP STEAM FOR CSO SHIFT R05 | STEAM | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
196 | 16 | 260 | PI-1101 | MP STEAM FOR CSO SHIFT R05 | STEAM | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
197 | 1.33 | 231.7 | FT-0502 | BRFORE CSO SHIFT FROM GUARD BED R04 | GAS | FT | 1/2" NPT (F) | 6" | SW | 1 | DP | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL
198 | 1.33 | 231.7 | PI-1103 | BRFORE CSO SHIFT FROM GUARD BED R05 | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
199 | 1.33 | 231.7 | TI-1102 | BRFORE CSO SHIFT FROM GUARD BED R06 | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
200 | 1.33 | 231.5 | PI-1102 | BEFORE GAURDE BED R04 FROM SYNGAS BAG FILETR | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
201 | 1.33 | 231.5 | TI-1101 | BEFORE GAURDE BED R04 FROM SYNGAS BAG FILETR | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
202 | 4.5 | 35 | PI-1106 | BEFORE BFW HEATER FROM HP BFW | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
203 | 4.5 | 35 | TI-1106 | BEFORE BFW HEATER FROM HP BFW | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
204 | 4.5 | 35 | TI-1107 | AFTER BFW HEATER TO FLASH VESSEL | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
205 | 4.5 | 35 | PI-1107 | AFTER BFW HEATER TO FLASH VESSEL | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
206 | 4.5 | 35 | TI-1108 | BEFORE SYNGAS COOLER, COOLING WATER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
207 | 4.5 | 35 | PI-1108 | BEFORE SYNGAS COOLER, COOLING WATER | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
208 | 4 | 45 | TI-1109 | AFTER SYNGAS COOLER, COOLING WATER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
209 | 4 | 45 | PI-1109 | AFTER SYNGAS COOLER, COOLING WATER | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
210 | 4.5 | 35 | TI-1110 | BEFORE CSO COOLER SO2, COOLING WATER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
211 | 4.5 | 35 | PI-1110 | BEFORE CSO COOLER SO2, COOLING WATER | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
212 | 4 | 45 | TI-1111 | AFTER CSO COOLER SO4, COOLING WATER | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
213 | 4 | 45 | PI-1111 | AFTER CSO COOLER SO4, COOLING WATER | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
214 |  |  | PI-1114 | BEFORE V04, CSO FROM SCRUBBER TANK | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
215 |  |  | TE-1113 | BEFORE V04, CSO FROM SCRUBBER TANK | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
216 |  |  | PI-1118 | BEFORE V04, NITROGEN FOM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
217 |  |  | PI-1119 | BEFORE V04, NITROGEN FOM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
218 |  |  | PS-1102 | V04 TANK | GAS | PS | 25 | - | SW | 1 | ELECTRIMECHANICAL/ SOLID-STATE | BAUMER/DANFOSS/INDFOS
219 |  |  | LG-1102 | V04 TANK | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
220 |  |  | TE-1102 | V04 TANK | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
221 |  |  | LT-1103 | V04 TANK | GAS | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
222 |  |  | LG-1104 | COLD CSO SEAL POT | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
11 | SYNGAS COMPRESSION SYSTEM
223 |  |  | PI-1210 | BEFORE KOD TANK V02, NITROGEN FROM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
224 |  |  | PI-1209 | BEFORE KOD TANK V02, NITROGEN FROM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
225 | 0.69 | 50.1 | PS-1201 | KOD TANK V02 | GAS | PS | 25 | - | SW | 1 | ELECTRIMECHANICAL/ SOLID-STATE | BAUMER/DANFOSS/INDFOS
226 | 0.69 | 50.1 | LG-1201 | KOD TANK V02 | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
227 | 0.69 | 50.1 | LT-1201 | KOD TANK V02 | GAS | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
228 | 0.69 | 50.1 | PI-1201 | KOD TANK V02 to 1st STAGE | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
229 | 0.69 | 50.1 | PT-1201 | KOD TANK V02 to 1st STAGE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
230 | 0.69 | 50.1 | TE-1201 | KOD TANK V02 to 1st STAGE | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
231 | 0.69 | 50.1 | TI-1202 | KOD TANK V02 to 1st STAGE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
232 | 1.64 | 50.2 | LG-1202 | INTERSTAGE KOD V03 | GAS | LG | 25 | - | FE, #150 | 1 | GLASS TUBE/REFLEX | FORBES/GENERAL/WAAREE
233 | 1.64 | 50.2 | LT-1202 | INTERSTAGE KOD V03 | GAS | LT | 1/2" NPT (F) | 6" | SW | 1 | DP | TEMPENSE/GIC/RADIX/ALTOP
234 | 1.64 | 50.2 | PS-1202 | INTERSTAGE KOD V03 | GAS | PS | 25 | - | SW | 1 | ELECTRIMECHANICAL/ SOLID-STATE | BAUMER/DANFOSS/INDFOS
235 |  |  | PI-1207 | BEFORE INTERSTAGE KOD V03 FROM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
236 |  |  | PI-1208 | BEFORE INTERSTAGE KOD V03 FROM NITROGEN PLANT | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
237 | 4 | 50.3 | PI-1206 | BEFORE INTERSTAGE KOD V03 TO SWS | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
238 | 4.5 | 35 | PI-1211 | BEFORE SYNGAS COOLER, COOLING WATER INLET | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
239 | 4.5 | 35 | TI-1209 | BEFORE SYNGAS COOLER, COOLING WATER INLET | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
240 | 4 | 45 | PI-1212 | AFTER SYNGAS COOLER, COOLING WATER OUTLET | WATER | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
241 | 4 | 45 | TI-1210 | AFTER SYNGAS COOLER, COOLING WATER OUTLET | WATER | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
242 | 1.79 | 107.9 | PI-1202 | AFTER SYNGAS COOLER, SYNGAS 1ST STAGE | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
243 | 1.79 | 107.9 | PT-1202 | AFTER SYNGAS COOLER, SYNGAS 1ST STAGE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
244 | 1.79 | 107.9 | TE-1203 | AFTER SYNGAS COOLER, SYNGAS 1ST STAGE | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
245 | 1.79 | 107.9 | TI-1204 | AFTER SYNGAS COOLER, SYNGAS 1ST STAGE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
246 | 3.01 | 98.5 | PI-1204 | BEFORE SRU INCINATOR, SYNGAS FROM 2ND STAGE | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
247 | 3.01 | 98.5 | PT-1204 | BEFORE SRU INCINATOR, SYNGAS FROM 2ND STAGE | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
248 | 3.01 | 98.5 | TI-1207 | BEFORE SRU INCINATOR, SYNGAS FROM 2ND STAGE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
249 | 3.01 | 98.5 | TI-1206 | BEFORE SRU INCINATOR, SYNGAS FROM 2ND STAGE | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE
250 | 1.69 | 50.3 | PI-1203 | BEFORE SYNGAS COOLER FROM INSTERSTAGE KOD V03 | GAS | PI | 1/2" NPT (F) | 6" | SW | 1 | BOURDON TUBE | FORBES/GENERAL/WAAREE
251 | 1.69 | 50.3 | PT-1203 | BEFORE SYNGAS COOLER FROM INSTERSTAGE KOD V03 | GAS | PT | 1/2" NPT (F) | 6" | SW | 1 | DIAPHARGM | ABB/E&H/YOKOGAWA/EMERSON/HONEYWELL/SIEMENS
252 | 1.69 | 50.3 | TE-1205 | BEFORE SYNGAS COOLER FROM INSTERSTAGE KOD V03 | GAS | TE | 1/2" NPT (F) | - | SW | 1 | RTD-PT100 | TEMPENSE/GIC/RADIX/ALTOP
253 | 1.69 | 50.3 | TI-1206 | BEFORE SYNGAS COOLER FROM INSTERSTAGE KOD V03 | GAS | TI | 1/2" NPT (F) | 6" | SW | 1 | Bi-METAL | FORBES/GENERAL/WAAREE